## 680-9-2
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
S&C Standard ("E") Speed (TCC 680-9-2) | [9 empty] | S&C Standard ("E") Speed (TCC 680-9-2)
Total Clearing Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated February 16, 2009
Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus.
25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 400E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04
16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.04 | 16000 | 0.0408 | 18000 | 0.0425 | 18000 | 0.0445 | 22000 | 0.0425
2652.0451 | 0.04 | 2925.1076 | 0.04 | 3755.8955 | 0.04 | 4578.3032 | 0.04 | 6267.1992 | 0.04 | 7935.375 | 0.04 | 9858.4531 | 0.04 | 12395.4571 | 0.04 | 15538.6268 | 0.04 | 17449.8248 | 0.04 | 14000 | 0.04115 | 12550 | 0.0485 | 15417.16 | 0.048 | 19716.95 | 0.0455
1948.4981 | 0.041 | 2149.1213 | 0.04115 | 2759.5139 | 0.04115 | 3363.7494 | 0.04115 | 4604.6071 | 0.04115 | 5830.2414 | 0.04115 | 7243.1563 | 0.04115 | 9107.1319 | 0.04115 | 11416.4668 | 0.04115 | 16000 | 0.0404 | 12500 | 0.04215 | 11409.86 | 0.0512 | 14961.43 | 0.049 | 18219.3 | 0.0474
1739.7304 | 0.042 | 1918.8583 | 0.04215 | 2463.8517 | 0.04215 | 3003.3477 | 0.04215 | 4111.2564 | 0.04215 | 5205.5727 | 0.04215 | 6467.1039 | 0.04215 | 8131.3678 | 0.04215 | 10193.2739 | 0.04215 | 12820.6533 | 0.04115 | 11250 | 0.04345 | 10129.812 | 0.05525 | 13991.89 | 0.0507 | 16337.75 | 0.051168
1565.7574 | 0.0433 | 1726.9725 | 0.04345 | 2217.4665 | 0.04345 | 2703.0129 | 0.04345 | 3700.1307 | 0.04345 | 4685.0154 | 0.04345 | 5820.3935 | 0.04345 | 7318.231 | 0.04345 | 9173.9465 | 0.04345 | 11447.0118 | 0.04215 | 10000 | 0.04515 | 8649.344 | 0.060938 | 12422.08 | 0.0548 | 15509.89 | 0.0528
1391.7843 | 0.045 | 1535.0867 | 0.04515 | 1971.0813 | 0.04515 | 2402.6782 | 0.04515 | 3289.0051 | 0.04515 | 4164.4581 | 0.04515 | 5173.6831 | 0.04515 | 6505.0942 | 0.04515 | 8154.6191 | 0.04515 | 10302.3106 | 0.04345 | 9527.41 | 0.046 | 7564.623 | 0.067456 | 10940.622 | 0.059877 | 13936.01 | 0.0572
1326.01 | 0.046 | 1462.54 | 0.046 | 1877.93 | 0.046 | 2289.13 | 0.046 | 3133.57 | 0.046 | 3967.65 | 0.046 | 4929.18 | 0.046 | 6197.67 | 0.046 | 7769.24 | 0.046 | 9157.6095 | 0.04515 | 9135.54 | 0.046942 | 6343.832 | 0.079001 | 9674.401 | 0.065396 | 12237.17 | 0.0632
1295.86 | 0.04645 | 1436.45 | 0.046377 | 1849.98 | 0.046325 | 2261.83 | 0.046284 | 3090.01 | 0.046336 | 3916.4 | 0.046325 | 4855.8 | 0.046377 | 6105.4 | 0.046346 | 7577.42 | 0.046492 | 8724.83 | 0.046 | 8475.44 | 0.048763 | 5570.488 | 0.090531 | 8503.539 | 0.073003 | 11273.79 | 0.0685
1222.83 | 0.047747 | 1396.78 | 0.046964 | 1798.89 | 0.04692 | 2208.19 | 0.046811 | 2980.74 | 0.047041 | 3800.65 | 0.046942 | 4731.17 | 0.046931 | 5877.74 | 0.04714 | 7079.28 | 0.047996 | 8509.41 | 0.046544 | 7792.59 | 0.051038 | 4723.18 | 0.11029 | 7504.354 | 0.082631 | 10564.323 | 0.073
1151.62 | 0.049271 | 1343.36 | 0.047829 | 1724.91 | 0.047829 | 2138.65 | 0.047514 | 2875.35 | 0.047889 | 3543.71 | 0.048599 | 4573.02 | 0.047688 | 5513.35 | 0.048687 | 6574.33 | 0.049882 | 8299.31 | 0.047063 | 7086.37 | 0.054239 | 4045.008 | 0.13593 | 6715.94 | 0.093016 | 9840.27 | 0.0786
1053.56 | 0.051841 | 1277.84 | 0.0491 | 1649.01 | 0.048956 | 2060.96 | 0.048386 | 2762.6 | 0.048827 | 3258.19 | 0.050903 | 4354.34 | 0.048879 | 5187.09 | 0.050333 | 6074.94 | 0.052274 | 8005.85 | 0.047901 | 6444.15 | 0.058078 | 3474.614 | 0.16962 | 5838.558 | 0.11036 | 9111.003 | 0.086
980.371 | 0.054276 | 1197.42 | 0.050933 | 1559.2 | 0.050463 | 1984.11 | 0.049378 | 2659.59 | 0.049868 | 3025.79 | 0.053194 | 4141.98 | 0.050248 | 4919.33 | 0.051936 | 5613.49 | 0.05506 | 7691.94 | 0.048905 | 5825.08 | 0.062939 | 3057.153 | 0.2076 | 5178.338 | 0.12962 | 8452.675 | 0.093763
897.785 | 0.057641 | 1120.94 | 0.053023 | 1453.79 | 0.052686 | 1893.02 | 0.050652 | 2464.95 | 0.052112 | 2787.58 | 0.056299 | 3789.27 | 0.053023 | 4554.76 | 0.054589 | 5064.08 | 0.059326 | 7397.73 | 0.049938 | 5235.604 | 0.070189 | 2633.95 | 0.2692 | 4342.646 | 0.16718 | 7904.897 | 0.101
829.589 | 0.06132 | 1042.03 | 0.05568 | 1298.45 | 0.056792 | 1781 | 0.05257 | 2296.01 | 0.054571 | 2542.56 | 0.060376 | 3536.63 | 0.055503 | 4276.66 | 0.057149 | 4684.1 | 0.063237 | 7058.08 | 0.051265 | 4737.37 | 0.079136 | 2331.428 | 0.34145 | 3809.443 | 0.20461 | 7297.147 | 0.11221
775 | 0.065417 | 962.882 | 0.059048 | 1185.51 | 0.060968 | 1685.69 | 0.054441 | 2125.85 | 0.057641 | 2385 | 0.064039 | 3261.45 | 0.05891 | 3987.53 | 0.06023 | 4338.301 | 0.068536 | 6788.11 | 0.05257 | 4189.086 | 0.092714 | 2080.243 | 0.4341 | 3355.11 | 0.25328 | 6844.761 | 0.12183
715 | 0.070625 | 898.683 | 0.062432 | 1100 | 0.065506 | 1576.44 | 0.057064 | 1935 | 0.062485 | 2137.168 | 0.071454 | 3045 | 0.062406 | 3700 | 0.06472 | 3937.252 | 0.076646 | 6418.43 | 0.054515 | 3798.036 | 0.10637 | 1837.638 | 0.57947 | 2963.829 | 0.3144 | 6362.895 | 0.13526
708.565 | 0.071955 | 830.6771 | 0.067472 | 1019.6769 | 0.070796 | 1496.56 | 0.059443 | 1750 | 0.069197 | 1964.985 | 0.079136 | 2760.692 | 0.06869 | 3185.094 | 0.076136 | 3584.009 | 0.086125 | 6142.14 | 0.056198 | 3440.041 | 0.12309 | 1652.816 | 0.75094 | 2561.218 | 0.40635 | 6022.379 | 0.14538
656.0532 | 0.078744 | 753.8861 | 0.075403 | 932.8473 | 0.078696 | 1393.99 | 0.062939 | 1559.679 | 0.078308 | 1795.86 | 0.088533 | 2470.655 | 0.078019 | 2833.413 | 0.088299 | 3217.104 | 0.099518 | 5830.91 | 0.058412 | 3169.21 | 0.13957 | 1500.026 | 0.9835 | 2255.748 | 0.51847 | 5576.065 | 0.16416
606.2188 | 0.086974 | 686.9357 | 0.084794 | 856.8318 | 0.087661 | 1335 | 0.065654 | 1428.295 | 0.087546 | 1671.098 | 0.097599 | 2273.865 | 0.086917 | 2548.447 | 0.10178 | 2905.144 | 0.11508 | 5546.53 | 0.060794 | 2910.963 | 0.15949 | 1365.452 | 1.2996 | 2061.598 | 0.6291 | 5246.087 | 0.18126
540.9041 | 0.10149 | 641.7774 | 0.092652 | 779.1795 | 0.099588 | 1240.459 | 0.071165 | 1309.286 | 0.098758 | 1565.938 | 0.10691 | 2047.221 | 0.099937 | 2315.17 | 0.11715 | 2545.895 | 0.14045 | 5239.22 | 0.06376 | 2668.413 | 0.18441 | 1274.405 | 1.627 | 1910.722 | 0.75094 | 4965.345 | 0.19832
494.3488 | 0.11585 | 600.1875 | 0.10156 | 712.8286 | 0.1129 | 1181.147 | 0.075403 | 1196.602 | 0.11215 | 1425.446 | 0.12263 | 1880.395 | 0.11265 | 2139.313 | 0.13227 | 2262.524 | 0.17013 | 4960.384 | 0.06736 | 2392.841 | 0.22125 | 1170.554 | 2.2408 | 1763.817 | 0.91445 | 4569.862 | 0.22916
454.0657 | 0.13115 | 547.9815 | 0.11593 | 642.4198 | 0.13206 | 1117.93 | 0.080734 | 1093.6112 | 0.12865 | 1315.853 | 0.13848 | 1720.268 | 0.12865 | 1990.692 | 0.14763 | 2047.221 | 0.20014 | 4709.034 | 0.07133 | 2195.655 | 0.2576 | 1094.7057 | 2.9813 | 1676.125 | 1.0519 | 4189.086 | 0.26874
421.256 | 0.14763 | 512.9828 | 0.12787 | 583.6149 | 0.15367 | 1049.6805 | 0.087777 | 952.644 | 0.15936 | 1212.255 | 0.1568 | 1578.511 | 0.14717 | 1865.413 | 0.1645 | 1859.825 | 0.23574 | 4470.422 | 0.075768 | 2000.669 | 0.30468 | 1026.8401 | 4.0542 | 1580.095 | 1.2275 | 3847.734 | 0.31883
390.8179 | 0.16654 | 473.5423 | 0.14496 | 533.918 | 0.17761 | 991.5224 | 0.094689 | 868.043 | 0.18612 | 1097.9947 | 0.18394 | 1425.446 | 0.17382 | 1721.995 | 0.18753 | 1686.212 | 0.27903 | 4252.402 | 0.080481 | 1833.964 | 0.36017 | 988.5513 | 5.1125 | 1482.129 | 1.4688 | 3562.57 | 0.37449
354.6895 | 0.19511 | 437.1345 | 0.16504 | 485.5301 | 0.20797 | 902.5654 | 0.10791 | 791.7459 | 0.21784 | 977.7372 | 0.22395 | 1301.454 | 0.20271 | 1608.794 | 0.21102 | 1471.789 | 0.35721 | 4012.778 | 0.086689 | 1734.084 | 0.4004 | 946.9449 | 6.9147 | 1373.669 | 1.8437 | 3204.267 | 0.47035
333.6993 | 0.2169 | 404.7384 | 0.18721 | 442.4123 | 0.24413 | 840.7047 | 0.11944 | 729.4133 | 0.25132 | 886.4647 | 0.26571 | 1198.989 | 0.2343 | 1482.129 | 0.24328 | 1326.413 | 0.43246 | 3794.241 | 0.093408 | 1633.104 | 0.45267 | 920.7979 | 9.3944 | 1285.933 | 2.2898 | 2972.739 | 0.55625
310.8281 | 0.24477 | 374.7436 | 0.21339 | 390.0369 | 0.30578 | 788.5856 | 0.13155 | 680.7812 | 0.28356 | 795.7147 | 0.32108 | 1129.172 | 0.26058 | 1393.029 | 0.27095 | 1176.428 | 0.54522 | 3591.192 | 0.10078 | 1558.128 | 0.499 | 893.585 | 12.504 | 1214.686 | 2.81 | 2805.22 | 0.6404
286.3575 | 0.28179 | 351.1596 | 0.23926 | 362.9417 | 0.34977 | 725.7756 | 0.15013 | 641.7774 | 0.31589 | 727.9569 | 0.37571 | 1065.5447 | 0.29076 | 1298.858 | 0.30688 | 1066.6106 | 0.66562 | 3395.612 | 0.10925 | 1485.099 | 0.55405 | 869.781 | 17.8693 | 1170.554 | 3.2809 | 2644.499 | 0.73826
261.9727 | 0.33054 | 323.8378 | 0.27557 | 337.3909 | 0.39892 | 667.3007 | 0.17197 | 597.1933 | 0.36017 | 686.2493 | 0.4194 | 1005.5012 | 0.32489 | 1224.432 | 0.34125 | 975.7836 | 0.80868 | 3194.664 | 0.11944 | 1419.748 | 0.61557 | 843.2314 | 26.3736 | 1119.052 | 4.1723 | 2528.141 | 0.83282
241.5897 | 0.38304 | 303.1545 | 0.31079 | 320.6148 | 0.44018 | 577.808 | 0.21878 | 561.8536 | 0.40077 | 650.1748 | 0.45949 | 952.644 | 0.36182 | 1141.657 | 0.38982 | 889.1278 | 0.99835 | 3023.702 | 0.12994 | 1353.209 | 0.68628 | 815.859 | 38.8178 | 1073.0291 | 5.4641 | 2402.433 | 0.9547
212.564 | 0.48241 | 274.3048 | 0.37295 | 305.5888 | 0.48196 | 504.3357 | 0.27804 | 531.2549 | 0.44347 | 616.6127 | 0.50847 | 881.1616 | 0.42057 | 1053.888 | 0.45352 | 818.3098 | 1.2187 | 2844.776 | 0.1428 | 1296.262 | 0.7626 | 790.1641 | 55.2337 | 1035.0868 | 7.2383 | 2258.003 | 1.1406
192.335 | 0.58203 | 253.7227 | 0.43166 | 294.195 | 0.52009 | 457.2546 | 0.33145 | 509.4045 | 0.48106 | 587.7146 | 0.55826 | 832.3403 | 0.4708 | 984.6056 | 0.52009 | 757.6646 | 1.4818 | 2689.841 | 0.15554 | 1230.57 | 0.8643 | 763.7509 | 82.1327 | 999.4864 | 9.9035 | 2139.313 | 1.3563
175.6051 | 0.68892 | 231.1903 | 0.5128 | 278.1724 | 0.57872 | 409.6246 | 0.40638 | 489.9191 | 0.52058 | 551.8304 | 0.6316 | 784.6531 | 0.5325 | 916.2054 | 0.60398 | 701.514 | 1.8122 | 2510.497 | 0.17397 | 1171.731 | 0.98108 | 734.5371 | 126.49 | 961.2559 | 14.1353 | 2008.688 | 1.6672
161.6186 | 0.80402 | 211.5036 | 0.60398 | 267.2648 | 0.6274 | 381.931 | 0.46424 | 470.7098 | 0.56091 | 521.2559 | 0.70898 | 740.4375 | 0.60055 | 872.3935 | 0.66816 | 640.4948 | 2.3646 | 2357.223 | 0.19346 | 1116.819 | 1.1088 | 706.442 | 192.108 | 935.6501 | 18.3024 | 1912.636 | 2.0575
150.843 | 0.91767 | 188.716 | 0.75169 | 257.8147 | 0.67522 | 361.493 | 0.5128 | 440.6457 | 0.63947 | 490.4097 | 0.80479 | 702.2158 | 0.67072 | 832.3403 | 0.7374 | 593.0276 | 3.0307 | 2202.255 | 0.2169 | 1070.8852 | 1.2451 | 685.564 | 281.742 | 907.9972 | 26.4791 | 1845.008 | 2.4723
140.9265 | 1.0552 | 173.5107 | 0.89316 | 246.9632 | 0.73669 | 343.8622 | 0.56357 | 417.8999 | 0.71512 | 461.3884 | 0.91501 | 669.9759 | 0.74166 | 794.1252 | 0.81886 | 549.0782 | 4.2542 | 2065.723 | 0.24158 | 1025.8127 | 1.4124 | 667.3007 | 386.432 | 890.9076 | 35.4094 | 1777.985 | 3.0708
131.3994 | 1.2116 | 163.8978 | 1.0032 | 234.6839 | 0.81808 | 330.3795 | 0.61091 | 389.6475 | 0.82919 | 439.3257 | 1.0159 | 626.5578 | 0.85848 | 765.2799 | 0.88885 | 516.5853 | 5.9708 | 1949.321 | 0.26784 | 981.6565 | 1.6249 | 650.8249 | 505.694 | 875.0148 | 49.0904 | 1721.995 | 3.8053
123.1296 | 1.385 | 153.89 | 1.1472 | 221.4597 | 0.92748 | 314.2667 | 0.67522 | 367.6904 | 0.93923 | 424.215 | 1.1013 | 597.7906 | 0.95389 | 735.273 | 0.97633 | 492.3754 | 8.2358 | 1846.856 | 0.29417 | 942.2226 | 1.861 | 641.7774 | 607.237 | 860.266 | 66.1188 | 1677.797 | 4.639
116.8904 | 1.5487 | 145.3639 | 1.2985 | 208.3543 | 1.0593 | 298.0439 | 0.74953 | 347.666 | 1.0593 | 407.99 | 1.2092 | 561.8536 | 1.1023 | 707.1493 | 1.0748 | 476.3924 | 10.9091 | 1760.297 | 0.32195 | 906.1833 | 2.1551 |  |  | 844.0751 | 90.2238 | 1639.649 | 5.7593
109.9739 | 1.7804 | 137.0358 | 1.4848 | 198.5896 | 1.1778 | 284.0761 | 0.826 | 327.4194 | 1.208 | 395.1409 | 1.296 | 530.7236 | 1.2598 | 678.0642 | 1.1905 | 464.6301 | 13.9294 | 1677.797 | 0.35395 | 875.0148 | 2.4917 |  |  | 830.6771 | 119.723 | 1608.794 | 6.8259
104.7152 | 1.9839 | 130.7438 | 1.6523 | 190.4221 | 1.2922 | 268.873 | 0.92569 | 310.2077 | 1.3676 | 382.3138 | 1.3987 | 504.3357 | 1.4249 | 657.3666 | 1.2871 | 454.9743 | 17.9308 | 1586.42 | 0.39525 | 849.1549 | 2.8531 |  |  | 816.6752 | 162.73 | 1565.938 | 8.6064
99.0123 | 2.2641 | 124.4914 | 1.8555 | 183.1379 | 1.4235 | 256.7851 | 1.0189 | 296.5578 | 1.5156 | 367.323 | 1.5441 | 486.0163 | 1.5578 | 633.4878 | 1.4207 | 443.7411 | 24.5833 | 1486.584 | 0.45056 | 818.3098 | 3.3998 |  |  | 804.5158 | 212.946 | 1534.929 | 10.5134
93.3395 | 2.6024 | 118.7758 | 2.0923 | 176.3091 | 1.5563 | 244.7511 | 1.1273 | 282.3766 | 1.7185 | 354.6895 | 1.69 | 472.5963 | 1.6768 | 615.3807 | 1.5246 | 434.5198 | 32.7127 | 1408.44 | 0.50371 | 791.7459 | 4.0003 |  |  | 795.7147 | 261.126 | 1501.522 | 12.8836
89.8592 | 2.8616 | 113.0965 | 2.3763 | 170.9279 | 1.6867 | 232.8139 | 1.2586 | 270.7628 | 1.9054 | 342.1473 | 1.85 | 456.3416 | 1.8464 | 595.4047 | 1.6752 | 428.9076 | 44.457 | 1342.429 | 0.55932 | 764.5143 | 4.9183 |  |  | 783.8688 | 337.299 | 1465.915 | 15.869
85.1355 | 3.2839 | 108.1202 | 2.6649 | 165.2134 | 1.8373 | 223.685 | 1.3878 | 263.2861 | 2.0556 | 330.7095 | 2.0214 | 439.7657 | 2.0374 | 572.6314 | 1.8738 | 422.0997 | 63.075 | 1260.468 | 0.6413 | 739.6972 | 6.0185 |  |  | 772.1978 | 431.361 | 1436.886 | 19.1621
80.7408 | 3.7991 | 103.6732 | 3.0008 | 160.4911 | 1.9722 | 212.7763 | 1.5593 | 254.7391 | 2.2485 | 318.3785 | 2.2441 | 421.256 | 2.2933 | 554.5969 | 2.0515 | 417.8999 | 81.795 | 1213.465 | 0.69954 | 715.6853 | 7.4253 |  |  | 764.5143 | 513.85 | 1400.014 | 24.3976
76.3436 | 4.4487 | 99.8075 | 3.3562 | 155.2815 | 2.1637 | 204.6374 | 1.7151 | 246.9632 | 2.4721 | 304.9783 | 2.5289 | 407.1738 | 2.5264 | 539.2838 | 2.2353 | 414.5702 | 110.401 | 1162.392 | 0.7774 | 695.9249 | 9.2359 |  |  | 759.9416 | 558.874 | 1373.669 | 29.1431
73.6441 | 4.9724 | 96.1821 | 3.7579 | 150.3909 | 2.3599 | 196.8109 | 1.8905 | 239.9045 | 2.6914 | 295.9649 | 2.7834 | 393.9573 | 2.7862 | 526.4952 | 2.4213 | 411.6783 | 141.325 | 1106.809 | 0.87776 | 681.4621 | 11.2068 |  |  | 757.6646 | 600.594 | 1341.087 | 36.0878
71.0401 | 5.5692 | 93.2462 | 4.1914 | 144.7831 | 2.6205 | 189.8512 | 2.08 | 231.6534 | 2.9742 | 284.3599 | 3.1407 | 380.0269 | 3.0944 | 515.5535 | 2.5973 | 409.2154 | 177.154 | 1064.4788 | 0.96973 | 664.6376 | 14.1253 |  |  |  |  | 1313.224 | 44.1571
68.5281 | 6.2942 | 90.5809 | 4.6799 | 139.6637 | 2.9304 | 181.6793 | 2.346 | 224.5815 | 3.2741 | 277.6169 | 3.4404 | 368.7948 | 3.4031 | 504.8395 | 2.839 | 405.1432 | 231.593 | 1022.7404 | 1.0779 | 643.0622 | 19.597 |  |  |  |  | 1276.957 | 57.7741
66.3699 | 7.0928 | 88.168 | 5.2518 | 134.3221 | 3.3034 | 173.5107 | 2.6675 | 216.4239 | 3.6405 | 268.6046 | 3.8599 | 359.6901 | 3.7208 | 494.8438 | 3.0944 | 402.7199 | 300.651 | 984.6056 | 1.1986 | 625.306 | 26.4427 |  |  |  |  | 1247.928 | 71.6224
64.5373 | 7.9536 | 85.4767 | 6.0006 | 128.7968 | 3.7728 | 166.2078 | 3.0097 | 209.6083 | 4.0482 | 264.077 | 4.2122 | 350.108 | 4.1049 | 485.045 | 3.3596 | 400.3109 | 377.636 | 950.7399 | 1.3293 | 611.0885 | 34.6297 |  |  |  |  | 1218.327 | 90.0436
62.8811 | 8.9104 | 83.3662 | 6.8091 | 125.2405 | 4.1914 | 160.171 | 3.3863 | 205.0477 | 4.4004 | 257.8147 | 4.666 | 343.519 | 4.4399 | 474.0164 | 3.7061 | 396 | 478.624 | 912.5479 | 1.5053 | 596.0009 | 47.346 |  |  |  |  | 1187.065 | 116.07
60.9616 | 10.2346 | 80.8216 | 8.1379 | 122.3937 | 4.5833 | 154.8162 | 3.7803 | 199.9844 | 4.8215 | 252.9626 | 5.1331 | 336.38 | 4.86 | 464.6301 | 4.0724 | 396 | 577.036 | 875.8904 | 1.7185 | 583.6149 | 63.2012 |  |  |  |  | 1161.237 | 142.47
59.5754 | 11.6746 | 78.6686 | 9.6596 | 119.7306 | 5.1127 | 150.5416 | 4.1253 | 195.6328 | 5.2675 | 248.4504 | 5.7208 | 329.3895 | 5.336 | 456.7981 | 4.431 | 396 | 600 | 838.1868 | 1.9878 | 572.0583 | 88.1632 |  |  |  |  | 1130.294 | 179.841
58.6885 | 13.1592 | 76.573 | 11.6979 | 117.2424 | 5.7436 | 147.5606 | 4.4531 | 191.1844 | 5.8648 | 243.287 | 6.4592 | 322.2219 | 5.9235 | 449.9968 | 4.7786 |  |  | 814.2288 | 2.2286 | 561.8536 | 120.193 |  |  |  |  | 1104.598 | 227.017
57.584 | 15.2535 | 74.6824 | 14.1818 | 114.3472 | 6.5433 | 144.7831 | 4.7928 | 187.3993 | 6.4463 | 237.2799 | 7.4179 | 316.7912 | 6.4785 | 442.4123 | 5.2102 |  |  | 787.798 | 2.5289 | 554.0425 | 161.101 |  |  |  |  | 1079.4872 | 279.498
56.5567 | 18.0926 | 72.9842 | 17.7349 | 112.6444 | 7.3152 | 142.3433 | 5.1947 | 183.5053 | 7.1924 | 232.8139 | 8.3849 | 311.1394 | 7.1353 | 435.8255 | 5.6698 |  |  | 765.2799 | 2.8531 | 546.887 | 227.689 |  |  |  |  | 1057.0538 | 339.668
55.659 | 22.0697 | 72.0416 | 19.9723 | 110.0836 | 8.5366 | 139.9442 | 5.6472 | 180.0513 | 7.9933 | 228.4326 | 9.5163 | 304.9783 | 7.8905 | 429.3366 | 6.238 |  |  | 744.8936 | 3.229 | 540.9041 | 310.427 |  |  |  |  | 1033.0188 | 424.939
55 | 26.5221 | 71.3962 | 22.5374 | 108.0122 | 9.8443 | 137.5847 | 6.2009 | 176.4862 | 8.9638 | 224.1338 | 11.0184 | 298.0439 | 9.0807 | 420.8347 | 7.0016 |  |  | 725.7756 | 3.6622 | 536.5943 | 403.803 |  |  |  |  | 1010.5414 | 519.533
55 | 32.1939 | 70.474 | 26.4956 | 105.8734 | 11.4098 | 135.1306 | 6.9253 | 174.0321 | 9.9728 | 219.9153 | 12.7585 | 292.435 | 10.1837 | 411.6783 | 7.9536 |  |  | 704.3256 | 4.2797 | 532.4 | 502.659 |  |  |  |  | 993.5068 | 597.002
55 | 39.7497 | 69.8426 | 30.4423 | 103.9848 | 13.3977 | 132.5874 | 7.7425 | 170.7563 | 11.1956 | 215.5604 | 15.1625 | 286.9306 | 11.5818 | 403.9299 | 8.9996 |  |  | 686.2493 | 4.9428 | 529.65 | 556.077 |  |  |  |  | 991.5224 | 613.339
55 | 49.0313 | 69.2168 | 35.3287 | 102.0276 | 16.2597 | 130.6129 | 8.6049 | 168.047 | 12.5564 | 210.87 | 18.165 | 281.5307 | 13.3843 | 398.7126 | 9.9331 |  |  | 668.6372 | 5.7722 | 528 | 600
55 | 65.06 | 68.5281 | 43.4468 | 99.5085 | 21.2055 | 128.5405 | 9.6596 | 165.8756 | 13.999 | 206.4876 | 22.7864 | 276.7853 | 15.3146 | 393.9573 | 11.0514 |  |  | 650.1748 | 6.9322
55 | 85.473 | 67.9141 | 54.2391 | 98.1252 | 25.5088 | 126.6265 | 10.844 | 163.57 | 15.4682 | 202.8037 | 28.4999 | 272.3919 | 17.3844 | 387.7038 | 12.5189 |  |  | 636.6635 | 7.9536
55 | 123.481 | 67.373 | 67.7139 | 97.0517 | 30.0195 | 124.9908 | 12.0532 | 161.4569 | 17.4539 | 199.1869 | 34.8728 | 268.0678 | 20.0322 | 381.931 | 14.2812 |  |  | 622.1875 | 9.4501
55 | 169.869 | 66.903 | 88.3396 | 95.7982 | 36.7693 | 123.2528 | 13.9433 | 159.5308 | 19.6951 | 195.8286 | 45.9017 | 262.4974 | 24.1935 | 376.6213 | 16.0181 |  |  | 609.8675 | 11.1622
55 | 227.917 | 66.3699 | 117.226 | 95.0348 | 43.0148 | 121.418 | 16.0021 | 157.6289 | 22.3581 | 192.72 | 59.2257 | 258.8476 | 27.7414 | 371.7571 | 18.2377 |  |  | 596.5971 | 13.3443
55 | 306.111 | 66.1712 | 161.263 | 93.9013 | 52.7422 | 119.9693 | 18.736 | 155.9041 | 25.9715 | 189.8512 | 75.5841 | 255.2495 | 32.0976 | 366.9556 | 20.9738 |  |  | 584.199 | 16.3574
55 | 429.2 | 66 | 210.396 | 93.06 | 67.1746 | 118.4205 | 21.9378 | 154.198 | 29.1914 | 187.3993 | 94.9325 | 251.7009 | 37.0644 | 360.4095 | 24.4853 |  |  | 574.926 | 18.9808
55 | 520.563 | 66 | 270.416 | 92.0419 | 85.9013 | 117.2424 | 25.3563 | 152.3588 | 34.3197 | 184.7934 | 124.224 | 248.2018 | 42.8432 | 355.0437 | 28.1884 |  |  | 565.8004 | 22.6955
55 | 600 | 66 | 332.6 | 90.7399 | 104.913 | 116.1919 | 29.6025 | 150.5416 | 40.7959 | 182.7727 | 159.339 | 245.2406 | 48.4468 | 350.4578 | 33.2398 |  |  | 555.7068 | 27.2199
|  | 66 | 414.853 | 89.7531 | 126.606 | 114.9203 | 35.8264 | 148.5968 | 53.4854 | 181.3163 | 207.057 | 242.3157 | 56.2824 | 345.2405 | 39.1583 |  |  | 547.9815 | 31.8421
|  | 66 | 491.231 | 88.86 | 155.096 | 114.0051 | 42.7577 | 147.4132 | 64.0918 | 180.0513 | 258.777 | 239.1862 | 64.4773 | 340.4412 | 46.922 |  |  | 538.2058 | 38.1541
|  | 66 | 566.177 | 88 | 201.542 | 113.0965 | 51.9056 | 146.2384 | 76.4198 | 178.7951 | 326.015 | 236.0963 | 76.6493 | 336.7166 | 57.3041 |  |  | 530.7236 | 45.7642
|  | 66 | 600 | 88 | 255.69 | 112.5322 | 61.1506 | 144.9283 | 98.1165 | 177.5477 | 415.268 | 233.5135 | 88.7823 | 333.6993 | 67.4437 |  |  | 522.8223 | 53.9148
|  | 66 | 600 | 88 | 336.279 | 111.6357 | 74.9072 | 144.0615 | 115.481 | 176 | 498.654 | 230.9593 | 101.61 | 330.3795 | 83.2801 |  |  | 515.0387 | 64.7356
|  |  |  | 88 | 422.388 | 111.3013 | 87.0249 | 143 | 141.042 | 176 | 559.423 | 228.2038 | 122.131 | 330 | 104.181 |  |  | 506.3564 | 85.473
|  |  |  | 88 | 513.84 | 110.7458 | 105.967 | 143 | 170.72 | 176 | 600 | 225.9334 | 146.797 | 330 | 127.623 |  |  | 498.8181 | 110.18
|  |  |  | 88 | 578.191 | 110.3036 | 127.496 | 143 | 216.37 |  |  | 223.685 | 178.22 | 330 | 167.675 |  |  | 492.3754 | 139.221
|  |  |  | 88 | 600 | 110 | 173.82 | 143 | 278.651 |  |  | 221.4597 | 209.138 | 330 | 205.202 |  |  | 485.5301 | 185.121
[6 empty] | 110 | 223.628 | 143 | 359.579 |  |  | 220.1353 | 251.632 | 330 | 271.5 |  |  | 480.6989 | 232.288
[6 empty] | 110 | 282.579 | 143 | 461.24 |  |  | 220 | 299.152 | 330 | 341.702 |  |  | 475.9161 | 300.952
[6 empty] | 110 | 347.908 | 143 | 569.584 |  |  | 220 | 362.105 | 330 | 418.603 |  |  | 469.4525 | 379.529
[6 empty] | 110 | 424.505 | 143 | 600 |  |  | 220 | 446.714 | 330 | 528.958 |  |  | 465.0624 | 486.343
[6 empty] | 110 | 488.292 |  |  |  |  | 220 | 553.857 | 330 | 577.614 |  |  | 462 | 570.154
[6 empty] | 110 | 569.014 |  |  |  |  | 220 | 600 | 330 | 600 |  |  | 462 | 600
[6 empty] | 110 | 600