## 691-9-U3
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
US Very Inverse (U3) (TCC 691-9-U3) | [9 empty] | US Very Inverse (U3) (TCC 691-9-U3) | [9 empty] | US Very Inverse (U3) (TCC 691-9-U3)
Average Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Average Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Average Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of
| current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5
| cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between
| 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting.
| Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup
| current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds.
Time Dial = 0.5 |  | Time Dial = 1.0 |  | Time Dial = 2.0 |  | Time Dial = 3.0 |  | Time Dial = 4.0 |  | Time Dial = 5.0 |  | Time Dial = 6.0 |  | Time Dial = 8.0 |  | Time Dial = 10.0 |  | Time Dial = 12.0 |  | Time Dial = 15.0
*of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s)
1.5 | 1.6001 | 1.5 | 3.2003 | 1.5 | 6.4006 | 1.5 | 9.6009 | 1.5 | 12.8012 | 1.5 | 16.0015 | 1.5 | 19.2018 | 1.5 | 25.6024 | 1.5 | 32.003 | 1.5 | 38.4036 | 1.5 | 48.0045
1.6 | 1.2917 | 1.6 | 2.5835 | 1.6 | 5.167 | 1.6 | 7.7504 | 1.6 | 10.3339 | 1.6 | 12.9174 | 1.6 | 15.5009 | 1.6 | 20.6678 | 1.6 | 25.8348 | 1.6 | 31.0018 | 1.6 | 38.7522
1.7 | 1.0746 | 1.7 | 2.1492 | 1.7 | 4.2984 | 1.7 | 6.4476 | 1.7 | 8.5968 | 1.7 | 10.7461 | 1.7 | 12.8953 | 1.7 | 17.1937 | 1.7 | 21.4921 | 1.7 | 25.7905 | 1.7 | 32.2382
1.8 | 0.91422 | 1.8 | 1.8284 | 1.8 | 3.6569 | 1.8 | 5.4853 | 1.8 | 7.3138 | 1.8 | 9.1422 | 1.8 | 10.9707 | 1.8 | 14.6275 | 1.8 | 18.2844 | 1.8 | 21.9413 | 1.8 | 27.4266
1.9 | 0.79145 | 1.9 | 1.5829 | 1.9 | 3.1658 | 1.9 | 4.7487 | 1.9 | 6.3316 | 1.9 | 7.9145 | 1.9 | 9.4973 | 1.9 | 12.6631 | 1.9 | 15.8289 | 1.9 | 18.9947 | 1.9 | 23.7434
2 | 0.69482 | 2 | 1.3896 | 2 | 2.7793 | 2 | 4.1689 | 2 | 5.5585 | 2 | 6.9482 | 2 | 8.3378 | 2 | 11.1171 | 2 | 13.8963 | 2 | 16.6756 | 2 | 20.8445
2.1 | 0.61706 | 2.1 | 1.2341 | 2.1 | 2.4683 | 2.1 | 3.7024 | 2.1 | 4.9365 | 2.1 | 6.1706 | 2.1 | 7.4048 | 2.1 | 9.873 | 2.1 | 12.3413 | 2.1 | 14.8096 | 2.1 | 18.5119
2.2 | 0.55336 | 2.2 | 1.1067 | 2.2 | 2.2134 | 2.2 | 3.3201 | 2.2 | 4.4269 | 2.2 | 5.5336 | 2.2 | 6.6403 | 2.2 | 8.8537 | 2.2 | 11.0672 | 2.2 | 13.2806 | 2.2 | 16.6008
2.3 | 0.50036 | 2.3 | 1.0007 | 2.3 | 2.0015 | 2.3 | 3.0022 | 2.3 | 4.0029 | 2.3 | 5.0036 | 2.3 | 6.0044 | 2.3 | 8.0058 | 2.3 | 10.0073 | 2.3 | 12.0087 | 2.3 | 15.0109
2.4 | 0.45571 | 2.4 | 0.91143 | 2.4 | 1.8229 | 2.4 | 2.7343 | 2.4 | 3.6457 | 2.4 | 4.5571 | 2.4 | 5.4686 | 2.4 | 7.2914 | 2.4 | 9.1143 | 2.4 | 10.9371 | 2.4 | 13.6714
2.5 | 0.41767 | 2.5 | 0.83535 | 2.5 | 1.6707 | 2.5 | 2.506 | 2.5 | 3.3414 | 2.5 | 4.1767 | 2.5 | 5.0121 | 2.5 | 6.6828 | 2.5 | 8.3535 | 2.5 | 10.0242 | 2.5 | 12.5302
2.6 | 0.38496 | 2.6 | 0.76991 | 2.6 | 1.5398 | 2.6 | 2.3097 | 2.6 | 3.0796 | 2.6 | 3.8496 | 2.6 | 4.6195 | 2.6 | 6.1593 | 2.6 | 7.6991 | 2.6 | 9.2389 | 2.6 | 11.5487
2.7 | 0.35658 | 2.7 | 0.71315 | 2.7 | 1.4263 | 2.7 | 2.1395 | 2.7 | 2.8526 | 2.7 | 3.5658 | 2.7 | 4.2789 | 2.7 | 5.7052 | 2.7 | 7.1315 | 2.7 | 8.5578 | 2.7 | 10.6973
2.8 | 0.33178 | 2.8 | 0.66355 | 2.8 | 1.3271 | 2.8 | 1.9907 | 2.8 | 2.6542 | 2.8 | 3.3178 | 2.8 | 3.9813 | 2.8 | 5.3084 | 2.8 | 6.6355 | 2.8 | 7.9626 | 2.8 | 9.9533
2.9 | 0.30996 | 2.9 | 0.61992 | 2.9 | 1.2398 | 2.9 | 1.8598 | 2.9 | 2.4797 | 2.9 | 3.0996 | 2.9 | 3.7195 | 2.9 | 4.9593 | 2.9 | 6.1992 | 2.9 | 7.439 | 2.9 | 9.2988
3 | 0.29065 | 3 | 0.5813 | 3 | 1.1626 | 3 | 1.7439 | 3 | 2.3252 | 3 | 2.9065 | 3 | 3.4878 | 3 | 4.6504 | 3 | 5.813 | 3 | 6.9756 | 3 | 8.7195
3.1 | 0.27347 | 3.1 | 0.54694 | 3.1 | 1.0939 | 3.1 | 1.6408 | 3.1 | 2.1878 | 3.1 | 2.7347 | 3.1 | 3.2816 | 3.1 | 4.3755 | 3.1 | 5.4694 | 3.1 | 6.5633 | 3.1 | 8.2041
3.2 | 0.25811 | 3.2 | 0.51621 | 3.2 | 1.0324 | 3.2 | 1.5486 | 3.2 | 2.0649 | 3.2 | 2.5811 | 3.2 | 3.0973 | 3.2 | 4.1297 | 3.2 | 5.1621 | 3.2 | 6.1946 | 3.2 | 7.7432
3.3 | 0.24431 | 3.3 | 0.48862 | 3.3 | 0.97723 | 3.3 | 1.4658 | 3.3 | 1.9545 | 3.3 | 2.4431 | 3.3 | 2.9317 | 3.3 | 3.9089 | 3.3 | 4.8862 | 3.3 | 5.8634 | 3.3 | 7.3292
3.4 | 0.23186 | 3.4 | 0.46372 | 3.4 | 0.92745 | 3.4 | 1.3912 | 3.4 | 1.8549 | 3.4 | 2.3186 | 3.4 | 2.7823 | 3.4 | 3.7098 | 3.4 | 4.6372 | 3.4 | 5.5647 | 3.4 | 6.9559
3.5 | 0.22059 | 3.5 | 0.44119 | 3.5 | 0.88238 | 3.5 | 1.3236 | 3.5 | 1.7648 | 3.5 | 2.2059 | 3.5 | 2.6471 | 3.5 | 3.5295 | 3.5 | 4.4119 | 3.5 | 5.2943 | 3.5 | 6.6178
3.6 | 0.21036 | 3.6 | 0.42071 | 3.6 | 0.84143 | 3.6 | 1.2621 | 3.6 | 1.6829 | 3.6 | 2.1036 | 3.6 | 2.5243 | 3.6 | 3.3657 | 3.6 | 4.2071 | 3.6 | 5.0486 | 3.6 | 6.3107
3.7 | 0.20103 | 3.7 | 0.40205 | 3.7 | 0.80411 | 3.7 | 1.2062 | 3.7 | 1.6082 | 3.7 | 2.0103 | 3.7 | 2.4123 | 3.7 | 3.2164 | 3.7 | 4.0205 | 3.7 | 4.8246 | 3.7 | 6.0308
3.8 | 0.1925 | 3.8 | 0.38499 | 3.8 | 0.76998 | 3.8 | 1.155 | 3.8 | 1.54 | 3.8 | 1.925 | 3.8 | 2.3099 | 3.8 | 3.0799 | 3.8 | 3.8499 | 3.8 | 4.6199 | 3.8 | 5.7749
3.9 | 0.18467 | 3.9 | 0.36935 | 3.9 | 0.73869 | 3.9 | 1.108 | 3.9 | 1.4774 | 3.9 | 1.8467 | 3.9 | 2.2161 | 3.9 | 2.9548 | 3.9 | 3.6935 | 3.9 | 4.4322 | 3.9 | 5.5402
4 | 0.17748 | 4 | 0.35497 | 4 | 0.70993 | 4 | 1.0649 | 4 | 1.4199 | 4 | 1.7748 | 4 | 2.1298 | 4 | 2.8397 | 4 | 3.5497 | 4 | 4.2596 | 4 | 5.3245
4.1 | 0.17086 | 4.1 | 0.34171 | 4.1 | 0.68343 | 4.1 | 1.0251 | 4.1 | 1.3669 | 4.1 | 1.7086 | 4.1 | 2.0503 | 4.1 | 2.7337 | 4.1 | 3.4171 | 4.1 | 4.1006 | 4.1 | 5.1257
4.2 | 0.16474 | 4.2 | 0.32947 | 4.2 | 0.65895 | 4.2 | 0.98842 | 4.2 | 1.3179 | 4.2 | 1.6474 | 4.2 | 1.9768 | 4.2 | 2.6358 | 4.2 | 3.2947 | 4.2 | 3.9537 | 4.2 | 4.9421
4.3 | 0.15907 | 4.3 | 0.31814 | 4.3 | 0.63628 | 4.3 | 0.95442 | 4.3 | 1.2726 | 4.3 | 1.5907 | 4.3 | 1.9088 | 4.3 | 2.5451 | 4.3 | 3.1814 | 4.3 | 3.8177 | 4.3 | 4.7721
4.4 | 0.15381 | 4.4 | 0.30763 | 4.4 | 0.61526 | 4.4 | 0.92289 | 4.4 | 1.2305 | 4.4 | 1.5381 | 4.4 | 1.8458 | 4.4 | 2.461 | 4.4 | 3.0763 | 4.4 | 3.6915 | 4.4 | 4.6144
4.5 | 0.14893 | 4.5 | 0.29786 | 4.5 | 0.59572 | 4.5 | 0.89358 | 4.5 | 1.1914 | 4.5 | 1.4893 | 4.5 | 1.7872 | 4.5 | 2.3829 | 4.5 | 2.9786 | 4.5 | 3.5743 | 4.5 | 4.4679
4.6 | 0.14438 | 4.6 | 0.28876 | 4.6 | 0.57752 | 4.6 | 0.86628 | 4.6 | 1.155 | 4.6 | 1.4438 | 4.6 | 1.7326 | 4.6 | 2.3101 | 4.6 | 2.8876 | 4.6 | 3.4651 | 4.6 | 4.3314
4.7 | 0.14014 | 4.7 | 0.28027 | 4.7 | 0.56055 | 4.7 | 0.84082 | 4.7 | 1.1211 | 4.7 | 1.4014 | 4.7 | 1.6816 | 4.7 | 2.2422 | 4.7 | 2.8027 | 4.7 | 3.3633 | 4.7 | 4.2041
4.8 | 0.13617 | 4.8 | 0.27234 | 4.8 | 0.54469 | 4.8 | 0.81703 | 4.8 | 1.0894 | 4.8 | 1.3617 | 4.8 | 1.6341 | 4.8 | 2.1787 | 4.8 | 2.7234 | 4.8 | 3.2681 | 4.8 | 4.0852
4.9 | 0.13246 | 4.9 | 0.26492 | 4.9 | 0.52984 | 4.9 | 0.79477 | 4.9 | 1.0597 | 4.9 | 1.3246 | 4.9 | 1.5895 | 4.9 | 2.1194 | 4.9 | 2.6492 | 4.9 | 3.1791 | 4.9 | 3.9738
5 | 0.12898 | 5 | 0.25797 | 5 | 0.51593 | 5 | 0.7739 | 5 | 1.0319 | 5 | 1.2898 | 5 | 1.5478 | 5 | 2.0637 | 5 | 2.5797 | 5 | 3.0956 | 5 | 3.8695
5.1 | 0.12572 | 5.1 | 0.25144 | 5.1 | 0.50288 | 5.1 | 0.75431 | 5.1 | 1.0058 | 5.1 | 1.2572 | 5.1 | 1.5086 | 5.1 | 2.0115 | 5.1 | 2.5144 | 5.1 | 3.0173 | 5.1 | 3.7716
5.2 | 0.12265 | 5.2 | 0.2453 | 5.2 | 0.4906 | 5.2 | 0.7359 | 5.2 | 0.98121 | 5.2 | 1.2265 | 5.2 | 1.4718 | 5.2 | 1.9624 | 5.2 | 2.453 | 5.2 | 2.9436 | 5.2 | 3.6795
5.3 | 0.11976 | 5.3 | 0.23953 | 5.3 | 0.47905 | 5.3 | 0.71858 | 5.3 | 0.95811 | 5.3 | 1.1976 | 5.3 | 1.4372 | 5.3 | 1.9162 | 5.3 | 2.3953 | 5.3 | 2.8743 | 5.3 | 3.5929
5.4 | 0.11704 | 5.4 | 0.23408 | 5.4 | 0.46817 | 5.4 | 0.70225 | 5.4 | 0.93634 | 5.4 | 1.1704 | 5.4 | 1.4045 | 5.4 | 1.8727 | 5.4 | 2.3408 | 5.4 | 2.809 | 5.4 | 3.5113
5.5 | 0.11447 | 5.5 | 0.22895 | 5.5 | 0.4579 | 5.5 | 0.68685 | 5.5 | 0.9158 | 5.5 | 1.1447 | 5.5 | 1.3737 | 5.5 | 1.8316 | 5.5 | 2.2895 | 5.5 | 2.7474 | 5.5 | 3.4342
5.6 | 0.11205 | 5.6 | 0.2241 | 5.6 | 0.4482 | 5.6 | 0.6723 | 5.6 | 0.8964 | 5.6 | 1.1205 | 5.6 | 1.3446 | 5.6 | 1.7928 | 5.6 | 2.241 | 5.6 | 2.6892 | 5.6 | 3.3615
5.7 | 0.10976 | 5.7 | 0.21951 | 5.7 | 0.43903 | 5.7 | 0.65854 | 5.7 | 0.87805 | 5.7 | 1.0976 | 5.7 | 1.3171 | 5.7 | 1.7561 | 5.7 | 2.1951 | 5.7 | 2.6342 | 5.7 | 3.2927
5.8 | 0.10759 | 5.8 | 0.21517 | 5.8 | 0.43035 | 5.8 | 0.64552 | 5.8 | 0.86069 | 5.8 | 1.0759 | 5.8 | 1.291 | 5.8 | 1.7214 | 5.8 | 2.1517 | 5.8 | 2.5821 | 5.8 | 3.2276
5.9 | 0.10553 | 5.9 | 0.21106 | 5.9 | 0.42212 | 5.9 | 0.63318 | 5.9 | 0.84424 | 5.9 | 1.0553 | 5.9 | 1.2664 | 5.9 | 1.6885 | 5.9 | 2.1106 | 5.9 | 2.5327 | 5.9 | 3.1659
6 | 0.10358 | 6 | 0.20716 | 6 | 0.41431 | 6 | 0.62147 | 6 | 0.82863 | 6 | 1.0358 | 6 | 1.2429 | 6 | 1.6573 | 6 | 2.0716 | 6 | 2.4859 | 6 | 3.1074
6.1 | 0.10173 | 6.1 | 0.20345 | 6.1 | 0.40691 | 6.1 | 0.61036 | 6.1 | 0.81381 | 6.1 | 1.0173 | 6.1 | 1.2207 | 6.1 | 1.6276 | 6.1 | 2.0345 | 6.1 | 2.4414 | 6.1 | 3.0518
6.2 | 0.099966 | 6.2 | 0.19993 | 6.2 | 0.39986 | 6.2 | 0.5998 | 6.2 | 0.79973 | 6.2 | 0.99966 | 6.2 | 1.1996 | 6.2 | 1.5995 | 6.2 | 1.9993 | 6.2 | 2.3992 | 6.2 | 2.999
6.3 | 0.098292 | 6.3 | 0.19658 | 6.3 | 0.39317 | 6.3 | 0.58975 | 6.3 | 0.78634 | 6.3 | 0.98292 | 6.3 | 1.1795 | 6.3 | 1.5727 | 6.3 | 1.9658 | 6.3 | 2.359 | 6.3 | 2.9488
6.4 | 0.096699 | 6.4 | 0.1934 | 6.4 | 0.38679 | 6.4 | 0.58019 | 6.4 | 0.77359 | 6.4 | 0.96699 | 6.4 | 1.1604 | 6.4 | 1.5472 | 6.4 | 1.934 | 6.4 | 2.3208 | 6.4 | 2.901
6.5 | 0.09518 | 6.5 | 0.19036 | 6.5 | 0.38072 | 6.5 | 0.57108 | 6.5 | 0.76144 | 6.5 | 0.9518 | 6.5 | 1.1422 | 6.5 | 1.5229 | 6.5 | 1.9036 | 6.5 | 2.2843 | 6.5 | 2.8554
6.6 | 0.093733 | 6.6 | 0.18747 | 6.6 | 0.37493 | 6.6 | 0.5624 | 6.6 | 0.74986 | 6.6 | 0.93733 | 6.6 | 1.1248 | 6.6 | 1.4997 | 6.6 | 1.8747 | 6.6 | 2.2496 | 6.6 | 2.812
6.7 | 0.092351 | 6.7 | 0.1847 | 6.7 | 0.36941 | 6.7 | 0.55411 | 6.7 | 0.73881 | 6.7 | 0.92351 | 6.7 | 1.1082 | 6.7 | 1.4776 | 6.7 | 1.847 | 6.7 | 2.2164 | 6.7 | 2.7705
6.8 | 0.091032 | 6.8 | 0.18206 | 6.8 | 0.36413 | 6.8 | 0.54619 | 6.8 | 0.72826 | 6.8 | 0.91032 | 6.8 | 1.0924 | 6.8 | 1.4565 | 6.8 | 1.8206 | 6.8 | 2.1848 | 6.8 | 2.731
6.9 | 0.089772 | 6.9 | 0.17954 | 6.9 | 0.35909 | 6.9 | 0.53863 | 6.9 | 0.71818 | 6.9 | 0.89772 | 6.9 | 1.0773 | 6.9 | 1.4364 | 6.9 | 1.7954 | 6.9 | 2.1545 | 6.9 | 2.6932
7 | 0.088567 | 7 | 0.17713 | 7 | 0.35427 | 7 | 0.5314 | 7 | 0.70853 | 7 | 0.88567 | 7 | 1.0628 | 7 | 1.4171 | 7 | 1.7713 | 7 | 2.1256 | 7 | 2.657
7.1 | 0.087413 | 7.1 | 0.17483 | 7.1 | 0.34965 | 7.1 | 0.52448 | 7.1 | 0.69931 | 7.1 | 0.87413 | 7.1 | 1.049 | 7.1 | 1.3986 | 7.1 | 1.7483 | 7.1 | 2.0979 | 7.1 | 2.6224
7.2 | 0.086309 | 7.2 | 0.17262 | 7.2 | 0.34524 | 7.2 | 0.51785 | 7.2 | 0.69047 | 7.2 | 0.86309 | 7.2 | 1.0357 | 7.2 | 1.3809 | 7.2 | 1.7262 | 7.2 | 2.0714 | 7.2 | 2.5893
7.3 | 0.085251 | 7.3 | 0.1705 | 7.3 | 0.341 | 7.3 | 0.5115 | 7.3 | 0.68201 | 7.3 | 0.85251 | 7.3 | 1.023 | 7.3 | 1.364 | 7.3 | 1.705 | 7.3 | 2.046 | 7.3 | 2.5575
7.4 | 0.084236 | 7.4 | 0.16847 | 7.4 | 0.33695 | 7.4 | 0.50542 | 7.4 | 0.67389 | 7.4 | 0.84236 | 7.4 | 1.0108 | 7.4 | 1.3478 | 7.4 | 1.6847 | 7.4 | 2.0217 | 7.4 | 2.5271
7.5 | 0.083263 | 7.5 | 0.16653 | 7.5 | 0.33305 | 7.5 | 0.49958 | 7.5 | 0.6661 | 7.5 | 0.83263 | 7.5 | 0.99916 | 7.5 | 1.3322 | 7.5 | 1.6653 | 7.5 | 1.9983 | 7.5 | 2.4979
7.6 | 0.082329 | 7.6 | 0.16466 | 7.6 | 0.32932 | 7.6 | 0.49397 | 7.6 | 0.65863 | 7.6 | 0.82329 | 7.6 | 0.98795 | 7.6 | 1.3173 | 7.6 | 1.6466 | 7.6 | 1.9759 | 7.6 | 2.4699
7.7 | 0.081432 | 7.7 | 0.16286 | 7.7 | 0.32573 | 7.7 | 0.48859 | 7.7 | 0.65145 | 7.7 | 0.81432 | 7.7 | 0.97718 | 7.7 | 1.3029 | 7.7 | 1.6286 | 7.7 | 1.9544 | 7.7 | 2.443
7.8 | 0.08057 | 7.8 | 0.16114 | 7.8 | 0.32228 | 7.8 | 0.48342 | 7.8 | 0.64456 | 7.8 | 0.8057 | 7.8 | 0.96684 | 7.8 | 1.2891 | 7.8 | 1.6114 | 7.8 | 1.9337 | 7.8 | 2.4171
7.9 | 0.079741 | 7.9 | 0.15948 | 7.9 | 0.31896 | 7.9 | 0.47845 | 7.9 | 0.63793 | 7.9 | 0.79741 | 7.9 | 0.95689 | 7.9 | 1.2759 | 7.9 | 1.5948 | 7.9 | 1.9138 | 7.9 | 2.3922
8 | 0.078944 | 8 | 0.15789 | 8 | 0.31577 | 8 | 0.47366 | 8 | 0.63155 | 8 | 0.78944 | 8 | 0.94732 | 8 | 1.2631 | 8 | 1.5789 | 8 | 1.8946 | 8 | 2.3683
8.1 | 0.078176 | 8.1 | 0.15635 | 8.1 | 0.31271 | 8.1 | 0.46906 | 8.1 | 0.62541 | 8.1 | 0.78176 | 8.1 | 0.93812 | 8.1 | 1.2508 | 8.1 | 1.5635 | 8.1 | 1.8762 | 8.1 | 2.3453
8.2 | 0.077437 | 8.2 | 0.15487 | 8.2 | 0.30975 | 8.2 | 0.46462 | 8.2 | 0.6195 | 8.2 | 0.77437 | 8.2 | 0.92925 | 8.2 | 1.239 | 8.2 | 1.5487 | 8.2 | 1.8585 | 8.2 | 2.3231
8.3 | 0.076726 | 8.3 | 0.15345 | 8.3 | 0.3069 | 8.3 | 0.46035 | 8.3 | 0.61381 | 8.3 | 0.76726 | 8.3 | 0.92071 | 8.3 | 1.2276 | 8.3 | 1.5345 | 8.3 | 1.8414 | 8.3 | 2.3018
8.4 | 0.07604 | 8.4 | 0.15208 | 8.4 | 0.30416 | 8.4 | 0.45624 | 8.4 | 0.60832 | 8.4 | 0.7604 | 8.4 | 0.91248 | 8.4 | 1.2166 | 8.4 | 1.5208 | 8.4 | 1.825 | 8.4 | 2.2812
8.5 | 0.075378 | 8.5 | 0.15076 | 8.5 | 0.30151 | 8.5 | 0.45227 | 8.5 | 0.60302 | 8.5 | 0.75378 | 8.5 | 0.90454 | 8.5 | 1.206 | 8.5 | 1.5076 | 8.5 | 1.8091 | 8.5 | 2.2613
8.6 | 0.07474 | 8.6 | 0.14948 | 8.6 | 0.29896 | 8.6 | 0.44844 | 8.6 | 0.59792 | 8.6 | 0.7474 | 8.6 | 0.89688 | 8.6 | 1.1958 | 8.6 | 1.4948 | 8.6 | 1.7938 | 8.6 | 2.2422
8.7 | 0.074124 | 8.7 | 0.14825 | 8.7 | 0.2965 | 8.7 | 0.44474 | 8.7 | 0.59299 | 8.7 | 0.74124 | 8.7 | 0.88949 | 8.7 | 1.186 | 8.7 | 1.4825 | 8.7 | 1.779 | 8.7 | 2.2237
8.8 | 0.073529 | 8.8 | 0.14706 | 8.8 | 0.29412 | 8.8 | 0.44118 | 8.8 | 0.58824 | 8.8 | 0.73529 | 8.8 | 0.88235 | 8.8 | 1.1765 | 8.8 | 1.4706 | 8.8 | 1.7647 | 8.8 | 2.2059
8.9 | 0.072955 | 8.9 | 0.14591 | 8.9 | 0.29182 | 8.9 | 0.43773 | 8.9 | 0.58364 | 8.9 | 0.72955 | 8.9 | 0.87546 | 8.9 | 1.1673 | 8.9 | 1.4591 | 8.9 | 1.7509 | 8.9 | 2.1887
9 | 0.0724 | 9 | 0.1448 | 9 | 0.2896 | 9 | 0.4344 | 9 | 0.5792 | 9 | 0.724 | 9 | 0.8688 | 9 | 1.1584 | 9 | 1.448 | 9 | 1.7376 | 9 | 2.172
9.1 | 0.071863 | 9.1 | 0.14373 | 9.1 | 0.28745 | 9.1 | 0.43118 | 9.1 | 0.57491 | 9.1 | 0.71863 | 9.1 | 0.86236 | 9.1 | 1.1498 | 9.1 | 1.4373 | 9.1 | 1.7247 | 9.1 | 2.1559
9.2 | 0.071345 | 9.2 | 0.14269 | 9.2 | 0.28538 | 9.2 | 0.42807 | 9.2 | 0.57076 | 9.2 | 0.71345 | 9.2 | 0.85614 | 9.2 | 1.1415 | 9.2 | 1.4269 | 9.2 | 1.7123 | 9.2 | 2.1403
9.3 | 0.070843 | 9.3 | 0.14169 | 9.3 | 0.28337 | 9.3 | 0.42506 | 9.3 | 0.56674 | 9.3 | 0.70843 | 9.3 | 0.85011 | 9.3 | 1.1335 | 9.3 | 1.4169 | 9.3 | 1.7002 | 9.3 | 2.1253
9.4 | 0.070357 | 9.4 | 0.14071 | 9.4 | 0.28143 | 9.4 | 0.42214 | 9.4 | 0.56286 | 9.4 | 0.70357 | 9.4 | 0.84428 | 9.4 | 1.1257 | 9.4 | 1.4071 | 9.4 | 1.6886 | 9.4 | 2.1107
9.5 | 0.069887 | 9.5 | 0.13977 | 9.5 | 0.27955 | 9.5 | 0.41932 | 9.5 | 0.55909 | 9.5 | 0.69887 | 9.5 | 0.83864 | 9.5 | 1.1182 | 9.5 | 1.3977 | 9.5 | 1.6773 | 9.5 | 2.0966
9.6 | 0.069431 | 9.6 | 0.13886 | 9.6 | 0.27773 | 9.6 | 0.41659 | 9.6 | 0.55545 | 9.6 | 0.69431 | 9.6 | 0.83318 | 9.6 | 1.1109 | 9.6 | 1.3886 | 9.6 | 1.6664 | 9.6 | 2.0829
9.7 | 0.06899 | 9.7 | 0.13798 | 9.7 | 0.27596 | 9.7 | 0.41394 | 9.7 | 0.55192 | 9.7 | 0.6899 | 9.7 | 0.82788 | 9.7 | 1.1038 | 9.7 | 1.3798 | 9.7 | 1.6558 | 9.7 | 2.0697
9.8 | 0.068562 | 9.8 | 0.13712 | 9.8 | 0.27425 | 9.8 | 0.41137 | 9.8 | 0.5485 | 9.8 | 0.68562 | 9.8 | 0.82275 | 9.8 | 1.097 | 9.8 | 1.3712 | 9.8 | 1.6455 | 9.8 | 2.0569
9.9 | 0.068148 | 9.9 | 0.1363 | 9.9 | 0.27259 | 9.9 | 0.40889 | 9.9 | 0.54518 | 9.9 | 0.68148 | 9.9 | 0.81778 | 9.9 | 1.0904 | 9.9 | 1.363 | 9.9 | 1.6356 | 9.9 | 2.0444
10 | 0.067746 | 10 | 0.13549 | 10 | 0.27098 | 10 | 0.40648 | 10 | 0.54197 | 10 | 0.67746 | 10 | 0.81295 | 10 | 1.0839 | 10 | 1.3549 | 10 | 1.6259 | 10 | 2.0324
10.5 | 0.065907 | 10.5 | 0.13181 | 10.5 | 0.26363 | 10.5 | 0.39544 | 10.5 | 0.52726 | 10.5 | 0.65907 | 10.5 | 0.79089 | 10.5 | 1.0545 | 10.5 | 1.3181 | 10.5 | 1.5818 | 10.5 | 1.9772
11 | 0.064317 | 11 | 0.12863 | 11 | 0.25727 | 11 | 0.3859 | 11 | 0.51453 | 11 | 0.64317 | 11 | 0.7718 | 11 | 1.0291 | 11 | 1.2863 | 11 | 1.5436 | 11 | 1.9295
11.5 | 0.062931 | 11.5 | 0.12586 | 11.5 | 0.25172 | 11.5 | 0.37759 | 11.5 | 0.50345 | 11.5 | 0.62931 | 11.5 | 0.75517 | 11.5 | 1.0069 | 11.5 | 1.2586 | 11.5 | 1.5103 | 11.5 | 1.8879
12 | 0.061716 | 12 | 0.12343 | 12 | 0.24687 | 12 | 0.3703 | 12 | 0.49373 | 12 | 0.61716 | 12 | 0.7406 | 12 | 0.98746 | 12 | 1.2343 | 12 | 1.4812 | 12 | 1.8515
12.5 | 0.060646 | 12.5 | 0.12129 | 12.5 | 0.24258 | 12.5 | 0.36388 | 12.5 | 0.48517 | 12.5 | 0.60646 | 12.5 | 0.72775 | 12.5 | 0.97034 | 12.5 | 1.2129 | 12.5 | 1.4555 | 12.5 | 1.8194
13 | 0.059698 | 13 | 0.1194 | 13 | 0.23879 | 13 | 0.35819 | 13 | 0.47758 | 13 | 0.59698 | 13 | 0.71637 | 13 | 0.95516 | 13 | 1.194 | 13 | 1.4327 | 13 | 1.7909
13.5 | 0.058853 | 13.5 | 0.11771 | 13.5 | 0.23541 | 13.5 | 0.35312 | 13.5 | 0.47083 | 13.5 | 0.58853 | 13.5 | 0.70624 | 13.5 | 0.94166 | 13.5 | 1.1771 | 13.5 | 1.4125 | 13.5 | 1.7656
14 | 0.058099 | 14 | 0.1162 | 14 | 0.23239 | 14 | 0.34859 | 14 | 0.46479 | 14 | 0.58099 | 14 | 0.69718 | 14 | 0.92958 | 14 | 1.162 | 14 | 1.3944 | 14 | 1.743
14.5 | 0.057421 | 14.5 | 0.11484 | 14.5 | 0.22968 | 14.5 | 0.34453 | 14.5 | 0.45937 | 14.5 | 0.57421 | 14.5 | 0.68905 | 14.5 | 0.91874 | 14.5 | 1.1484 | 14.5 | 1.3781 | 14.5 | 1.7226
15 | 0.056811 | 15 | 0.11362 | 15 | 0.22724 | 15 | 0.34086 | 15 | 0.45449 | 15 | 0.56811 | 15 | 0.68173 | 15 | 0.90897 | 15 | 1.1362 | 15 | 1.3635 | 15 | 1.7043
16 | 0.055758 | 16 | 0.11152 | 16 | 0.22303 | 16 | 0.33455 | 16 | 0.44606 | 16 | 0.55758 | 16 | 0.66909 | 16 | 0.89213 | 16 | 1.1152 | 16 | 1.3382 | 16 | 1.6727
17 | 0.054886 | 17 | 0.10977 | 17 | 0.21954 | 17 | 0.32932 | 17 | 0.43909 | 17 | 0.54886 | 17 | 0.65863 | 17 | 0.87818 | 17 | 1.0977 | 17 | 1.3173 | 17 | 1.6466
18 | 0.054156 | 18 | 0.10831 | 18 | 0.21662 | 18 | 0.32494 | 18 | 0.43325 | 18 | 0.54156 | 18 | 0.64987 | 18 | 0.8665 | 18 | 1.0831 | 18 | 1.2997 | 18 | 1.6247
19 | 0.053539 | 19 | 0.10708 | 19 | 0.21416 | 19 | 0.32123 | 19 | 0.42831 | 19 | 0.53539 | 19 | 0.64247 | 19 | 0.85662 | 19 | 1.0708 | 19 | 1.2849 | 19 | 1.6062
20 | 0.053012 | 20 | 0.10602 | 20 | 0.21205 | 20 | 0.31807 | 20 | 0.4241 | 20 | 0.53012 | 20 | 0.63615 | 20 | 0.84819 | 20 | 1.0602 | 20 | 1.2723 | 20 | 1.5904
21 | 0.052559 | 21 | 0.10512 | 21 | 0.21024 | 21 | 0.31535 | 21 | 0.42047 | 21 | 0.52559 | 21 | 0.63071 | 21 | 0.84095 | 21 | 1.0512 | 21 | 1.2614 | 21 | 1.5768
22 | 0.052167 | 22 | 0.10433 | 22 | 0.20867 | 22 | 0.313 | 22 | 0.41733 | 22 | 0.52167 | 22 | 0.626 | 22 | 0.83467 | 22 | 1.0433 | 22 | 1.252 | 22 | 1.565
23 | 0.051824 | 23 | 0.10365 | 23 | 0.2073 | 23 | 0.31095 | 23 | 0.41459 | 23 | 0.51824 | 23 | 0.62189 | 23 | 0.82919 | 23 | 1.0365 | 23 | 1.2438 | 23 | 1.5547
24 | 0.051524 | 24 | 0.10305 | 24 | 0.2061 | 24 | 0.30914 | 24 | 0.41219 | 24 | 0.51524 | 24 | 0.61829 | 24 | 0.82438 | 24 | 1.0305 | 24 | 1.2366 | 24 | 1.5457
25 | 0.051259 | 25 | 0.10252 | 25 | 0.20504 | 25 | 0.30755 | 25 | 0.41007 | 25 | 0.51259 | 25 | 0.61511 | 25 | 0.82014 | 25 | 1.0252 | 25 | 1.2302 | 25 | 1.5378
26 | 0.051024 | 26 | 0.10205 | 26 | 0.2041 | 26 | 0.30614 | 26 | 0.40819 | 26 | 0.51024 | 26 | 0.61229 | 26 | 0.81639 | 26 | 1.0205 | 26 | 1.2246 | 26 | 1.5307
27 | 0.050815 | 27 | 0.10163 | 27 | 0.20326 | 27 | 0.30489 | 27 | 0.40652 | 27 | 0.50815 | 27 | 0.60978 | 27 | 0.81304 | 27 | 1.0163 | 27 | 1.2196 | 27 | 1.5244
28 | 0.050628 | 28 | 0.10126 | 28 | 0.20251 | 28 | 0.30377 | 28 | 0.40502 | 28 | 0.50628 | 28 | 0.60753 | 28 | 0.81004 | 28 | 1.0126 | 28 | 1.2151 | 28 | 1.5188
29 | 0.05046 | 29 | 0.10092 | 29 | 0.20184 | 29 | 0.30276 | 29 | 0.40368 | 29 | 0.5046 | 29 | 0.60551 | 29 | 0.80735 | 29 | 1.0092 | 29 | 1.211 | 29 | 1.5138
30 | 0.050308 | 30 | 0.10062 | 30 | 0.20123 | 30 | 0.30185 | 30 | 0.40246 | 30 | 0.50308 | 30 | 0.6037 | 30 | 0.80493 | 30 | 1.0062 | 30 | 1.2074 | 30 | 1.5092
31 | 0.050308 | 31 | 0.10062 | 31 | 0.20123 | 31 | 0.30185 | 31 | 0.40246 | 31 | 0.50308 | 31 | 0.6037 | 31 | 0.80493 | 31 | 1.0062 | 31 | 1.2074 | 31 | 1.5092
32 | 0.050308 | 32 | 0.10062 | 32 | 0.20123 | 32 | 0.30185 | 32 | 0.40246 | 32 | 0.50308 | 32 | 0.6037 | 32 | 0.80493 | 32 | 1.0062 | 32 | 1.2074 | 32 | 1.5092
33 | 0.050308 | 33 | 0.10062 | 33 | 0.20123 | 33 | 0.30185 | 33 | 0.40246 | 33 | 0.50308 | 33 | 0.6037 | 33 | 0.80493 | 33 | 1.0062 | 33 | 1.2074 | 33 | 1.5092
34 | 0.050308 | 34 | 0.10062 | 34 | 0.20123 | 34 | 0.30185 | 34 | 0.40246 | 34 | 0.50308 | 34 | 0.6037 | 34 | 0.80493 | 34 | 1.0062 | 34 | 1.2074 | 34 | 1.5092
35 | 0.050308 | 35 | 0.10062 | 35 | 0.20123 | 35 | 0.30185 | 35 | 0.40246 | 35 | 0.50308 | 35 | 0.6037 | 35 | 0.80493 | 35 | 1.0062 | 35 | 1.2074 | 35 | 1.5092
36 | 0.050308 | 36 | 0.10062 | 36 | 0.20123 | 36 | 0.30185 | 36 | 0.40246 | 36 | 0.50308 | 36 | 0.6037 | 36 | 0.80493 | 36 | 1.0062 | 36 | 1.2074 | 36 | 1.5092
37 | 0.050308 | 37 | 0.10062 | 37 | 0.20123 | 37 | 0.30185 | 37 | 0.40246 | 37 | 0.50308 | 37 | 0.6037 | 37 | 0.80493 | 37 | 1.0062 | 37 | 1.2074 | 37 | 1.5092
38 | 0.050308 | 38 | 0.10062 | 38 | 0.20123 | 38 | 0.30185 | 38 | 0.40246 | 38 | 0.50308 | 38 | 0.6037 | 38 | 0.80493 | 38 | 1.0062 | 38 | 1.2074 | 38 | 1.5092
39 | 0.050308 | 39 | 0.10062 | 39 | 0.20123 | 39 | 0.30185 | 39 | 0.40246 | 39 | 0.50308 | 39 | 0.6037 | 39 | 0.80493 | 39 | 1.0062 | 39 | 1.2074 | 39 | 1.5092
40 | 0.050308 | 40 | 0.10062 | 40 | 0.20123 | 40 | 0.30185 | 40 | 0.40246 | 40 | 0.50308 | 40 | 0.6037 | 40 | 0.80493 | 40 | 1.0062 | 40 | 1.2074 | 40 | 1.5092
41 | 0.050308 | 41 | 0.10062 | 41 | 0.20123 | 41 | 0.30185 | 41 | 0.40246 | 41 | 0.50308 | 41 | 0.6037 | 41 | 0.80493 | 41 | 1.0062 | 41 | 1.2074 | 41 | 1.5092
42 | 0.050308 | 42 | 0.10062 | 42 | 0.20123 | 42 | 0.30185 | 42 | 0.40246 | 42 | 0.50308 | 42 | 0.6037 | 42 | 0.80493 | 42 | 1.0062 | 42 | 1.2074 | 42 | 1.5092
43 | 0.050308 | 43 | 0.10062 | 43 | 0.20123 | 43 | 0.30185 | 43 | 0.40246 | 43 | 0.50308 | 43 | 0.6037 | 43 | 0.80493 | 43 | 1.0062 | 43 | 1.2074 | 43 | 1.5092
44 | 0.050308 | 44 | 0.10062 | 44 | 0.20123 | 44 | 0.30185 | 44 | 0.40246 | 44 | 0.50308 | 44 | 0.6037 | 44 | 0.80493 | 44 | 1.0062 | 44 | 1.2074 | 44 | 1.5092
45 | 0.050308 | 45 | 0.10062 | 45 | 0.20123 | 45 | 0.30185 | 45 | 0.40246 | 45 | 0.50308 | 45 | 0.6037 | 45 | 0.80493 | 45 | 1.0062 | 45 | 1.2074 | 45 | 1.5092
46 | 0.050308 | 46 | 0.10062 | 46 | 0.20123 | 46 | 0.30185 | 46 | 0.40246 | 46 | 0.50308 | 46 | 0.6037 | 46 | 0.80493 | 46 | 1.0062 | 46 | 1.2074 | 46 | 1.5092
47 | 0.050308 | 47 | 0.10062 | 47 | 0.20123 | 47 | 0.30185 | 47 | 0.40246 | 47 | 0.50308 | 47 | 0.6037 | 47 | 0.80493 | 47 | 1.0062 | 47 | 1.2074 | 47 | 1.5092
48 | 0.050308 | 48 | 0.10062 | 48 | 0.20123 | 48 | 0.30185 | 48 | 0.40246 | 48 | 0.50308 | 48 | 0.6037 | 48 | 0.80493 | 48 | 1.0062 | 48 | 1.2074 | 48 | 1.5092
49 | 0.050308 | 49 | 0.10062 | 49 | 0.20123 | 49 | 0.30185 | 49 | 0.40246 | 49 | 0.50308 | 49 | 0.6037 | 49 | 0.80493 | 49 | 1.0062 | 49 | 1.2074 | 49 | 1.5092
50 | 0.050308 | 50 | 0.10062 | 50 | 0.20123 | 50 | 0.30185 | 50 | 0.40246 | 50 | 0.50308 | 50 | 0.6037 | 50 | 0.80493 | 50 | 1.0062 | 50 | 1.2074 | 50 | 1.5092
55 | 0.050308 | 55 | 0.10062 | 55 | 0.20123 | 55 | 0.30185 | 55 | 0.40246 | 55 | 0.50308 | 55 | 0.6037 | 55 | 0.80493 | 55 | 1.0062 | 55 | 1.2074 | 55 | 1.5092
60 | 0.050308 | 60 | 0.10062 | 60 | 0.20123 | 60 | 0.30185 | 60 | 0.40246 | 60 | 0.50308 | 60 | 0.6037 | 60 | 0.80493 | 60 | 1.0062 | 60 | 1.2074 | 60 | 1.5092
65 | 0.050308 | 65 | 0.10062 | 65 | 0.20123 | 65 | 0.30185 | 65 | 0.40246 | 65 | 0.50308 | 65 | 0.6037 | 65 | 0.80493 | 65 | 1.0062 | 65 | 1.2074 | 65 | 1.5092
70 | 0.050308 | 70 | 0.10062 | 70 | 0.20123 | 70 | 0.30185 | 70 | 0.40246 | 70 | 0.50308 | 70 | 0.6037 | 70 | 0.80493 | 70 | 1.0062 | 70 | 1.2074 | 70 | 1.5092
75 | 0.050308 | 75 | 0.10062 | 75 | 0.20123 | 75 | 0.30185 | 75 | 0.40246 | 75 | 0.50308 | 75 | 0.6037 | 75 | 0.80493 | 75 | 1.0062 | 75 | 1.2074 | 75 | 1.5092
80 | 0.050308 | 80 | 0.10062 | 80 | 0.20123 | 80 | 0.30185 | 80 | 0.40246 | 80 | 0.50308 | 80 | 0.6037 | 80 | 0.80493 | 80 | 1.0062 | 80 | 1.2074 | 80 | 1.5092
85 | 0.050308 | 85 | 0.10062 | 85 | 0.20123 | 85 | 0.30185 | 85 | 0.40246 | 85 | 0.50308 | 85 | 0.6037 | 85 | 0.80493 | 85 | 1.0062 | 85 | 1.2074 | 85 | 1.5092
90 | 0.050308 | 90 | 0.10062 | 90 | 0.20123 | 90 | 0.30185 | 90 | 0.40246 | 90 | 0.50308 | 90 | 0.6037 | 90 | 0.80493 | 90 | 1.0062 | 90 | 1.2074 | 90 | 1.5092
95 | 0.050308 | 95 | 0.10062 | 95 | 0.20123 | 95 | 0.30185 | 95 | 0.40246 | 95 | 0.50308 | 95 | 0.6037 | 95 | 0.80493 | 95 | 1.0062 | 95 | 1.2074 | 95 | 1.5092
100 | 0.050308 | 100 | 0.10062 | 100 | 0.20123 | 100 | 0.30185 | 100 | 0.40246 | 100 | 0.50308 | 100 | 0.6037 | 100 | 0.80493 | 100 | 1.0062 | 100 | 1.2074 | 100 | 1.5092